## Home
Kertas Kerja Perhitungan Efektifitas BAT
| Unit Pembangkit |  |  | : | UBJOM Tanjung Awar - Awar
| Lokasi |  |  | : | Tanjung Awar Awar - Tuban
| Tipe Pembangkit |  |  | : | Pembangkit Listrik Tenaga Uap
| Kapasitas |  |  | : | 2 x 350 MW
| Date |  |  | : | {{ home.date }}
UNIT#1 | [9 empty] | UNIT#2
| Enable Hours Modul BAT | [6 empty] | : | 1192.0 |  | Enable Hours Modul BAT |  |  | : | 1332.0
| Periode Hours | [6 empty] | : | 1440.0 |  | Periode Hours |  |  | : | 1440.0
| Durasi Pengurang Periode Hours | [6 empty] | : | 1.0 |  | Durasi Pengurang Periode Hours |  |  | : | 0.0
| a. | Gangguan Unit | [5 empty] | : | 1.0 |  | a. | Gangguan Unit |  | : | 0.0
|  | a.1 | Perbaikan equipment terkait BAT (Status Waiting Unit Shutdown/Sistem BAT outservice) |  |  |  |  | : | - |  |  | a.1 | Perbaikan equipment terkait BAT (Status Waiting Unit Shutdown/Sistem BAT outservice) | : | -
|  | a.2 | Maintenance Modul BAT yang membutuhkan Modul disable |  |  |  |  | : | - |  |  | a.2 | Maintenance Modul BAT yang membutuhkan Modul disable | : | -
| b. | Load < 70% | [5 empty] | : | 1440 |  | b. | Load < 70% |  | : | 1440
| c. | Pelaksanaan Uji Performance Test Unit | [5 empty] | : | - |  | c. | Pelaksanaan Uji Performance Test Unit |  | : | -
| Available Hours (Efektif) | [6 empty] | : | 1439.0 |  | Available Hours (Efektif) |  |  | : | 1440.0
| Efektifitas Modul BAT |  |  | = | Jumlah Enable Hours Modul BAT |  |  | x | 100%
Jumlah Available Hours (Efektif) Modul BAT
|  |  |  | = | 2524.0 | x | 100%
2879.0
|  |  |  | = | 87.67 %

## 1
[5 empty] | SISTEM PENGOPTIMUMAN KEANDALAN & EFISIENSI TERINTEGRASI (SOKET) | [7 empty] | Form No. | Date
2022-04-14
[13 empty] | Report No. | Page
of
Project No.:
[5 empty] | C l i e n t : |  | PT. Pembangkit Jawa Bali
DAILY REPORT MONITORING BOILER AUTO TUNING
Unit Pembangkit |  |  |  |  | : | UBJOM Tanjung Awar Awar
Lokasi |  |  |  |  | : | Tanjung Awar Awar
Tipe Pembangkit |  |  |  |  | : | Pembangkit Listrik Tenaga Uap
Kapasitas |  |  |  |  | : | 2 x 350 MW
Area |  |  |  |  | : | Unit - 1
Sub Area |  |  |  |  | : | Boiler
Tanggal |  |  |  |  | : | 2022-04-14 00:00 to 2022-04-14 23:59
NO. |  | ITEM TO CHECK | [7 empty] | ENABLE | DISABLE |  | REMARKS
1 |  | Boiler Auto Tuning Enable Status | [6 empty] | Min | 1192.0 | 248.0
|  |  | Sootblow Optimization Enable Status | [5 empty] | Min | 1192.0 | 248.0
|  |  | Combustion Optimization Enable Status | [5 empty] | Min | 0.0 | 1440.0
2 |  | Impossible Condition to Enable
|  |  | - | WatchdogStatus |  |  |  |  | Min | {{ s1.U28 }} | {{ s1.AD28 }}
|  |  | Sootblow Optimization Safeguard Violated | [5 empty] | Min
|  |  | - | BOILER DRUM LEVEL 3<120 |  |  |  |  | Min | 1440 | 0
|  |  | - | BOILER MFT TURB TRIP(SOE)=0 |  |  |  |  | Min | 1440 | 0
|  |  | - | FURNACE PRESS #1< -10 |  |  |  |  | Min | 1439 | 1
|  |  | - | GEN ACTIVE POWER>240 |  |  |  |  | Min | 1440 | 0
|  |  | Combustion Optimization Safeguard Violated | [5 empty] | Min
|  |  | - | BOILER DRUM LEVEL 3<120 |  |  |  |  | Min | 1440 | 0
|  |  | - | BOILER MFT TURB TRIP(SOE)=0 |  |  |  |  | Min | 1440 | 0
|  |  | - | FEGT<1300 |  |  |  |  | Min | 1440 | 0
|  |  | - | FURNACE PRESS #1< -10 |  |  |  |  | Min | 1439 | 1
|  |  | - | GEN ACTIVE POWER>240 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 FD FAN MOVABLE BLADE POSI> 5 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 ID FAN FIXED BLADE POSI<97 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 ID FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 PA FAN MOT CURRENT<205 |  |  |  |  | Min | 1439 | 1
|  |  | - | No.1 PA FAN MOT CURRENT<250 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.2 ID FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.2 PA FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No1 FD FAN MOT CURRENT<42 |  |  |  |  | Min | 1440 | 0
|  |  | - | No1 FD FAN MOT CURRENT>23 |  |  |  |  | Min | 1440 | 0
|  |  | - | No2 FD FAN MOT CURRENT<42 |  |  |  |  | Min | 1440 | 0
|  |  | - | No2 FD FAN MOT CURRENT>23 |  |  |  |  | Min | 1440 | 0
|  |  | - | SH.FIN.OUT HEADER L OUT GAS TEMP<800 |  |  |  |  | Min | 1440 | 0
|  |  | - | [5 empty] | Min
3 |  | Total Possible Condition Time | [6 empty] | Min | 1439.0 | 1.0
|  |  | - | Sootblow Optimization |  |  |  |  | Min | 1439.0 | 1.0
|  |  | - | Combustion Optimization |  |  |  |  | Min | 1438.0 | 2.0
4 |  | Percentage of BAT Enabled | [6 empty] | % | 82.84 | 17.16
|  |  | Percentage of Sootblow Optimization Enabled | [5 empty] | % | 82.84 | 17.16
|  |  | Percentage of Combustion Optimization Enabled | [5 empty] | % | 0.0 | 100.0
Remarks : |  |  |  | This document is generated by bot on 2022-04-15 02:02:55.
|  |  |  | Prepared by |  |  |  | Checked by |  |  |  | Witnessed / Approved by
PT . SARANA MAJU LESTARI
Name
Signature
Date

## 2
[5 empty] | SISTEM PENGOPTIMUMAN KEANDALAN & EFISIENSI TERINTEGRASI (SOKET) | [7 empty] | Form No. | Date
2022-04-14
[13 empty] | Report No. | Page
of
Project No.:
[5 empty] | C l i e n t : |  | PT. Pembangkit Jawa Bali
DAILY REPORT MONITORING BOILER AUTO TUNING
Unit Pembangkit |  |  |  |  | : | UBJOM Tanjung Awar Awar
Lokasi |  |  |  |  | : | Tanjung Awar Awar
Tipe Pembangkit |  |  |  |  | : | Pembangkit Listrik Tenaga Uap
Kapasitas |  |  |  |  | : | 2 x 350 MW
Area |  |  |  |  | : | Unit - 2
Sub Area |  |  |  |  | : | Boiler
Tanggal |  |  |  |  | : | 2022-04-14 00:00 to 2022-04-14 23:59
NO. |  | ITEM TO CHECK | [7 empty] | ENABLE | DISABLE |  | REMARKS
1 |  | Boiler Auto Tuning Enable Status | [6 empty] | Min | 1332.0 | 108.0
|  |  | Sootblow Optimization Enable Status | [5 empty] | Min | 1332.0 | 108.0
|  |  | Combustion Optimization Enable Status | [5 empty] | Min | 0.0 | 1440.0
2 |  | Impossible Condition to Enable
|  |  | - | WatchdogStatus |  |  |  |  | Min | {{ s2.U28 }} | {{ s2.AD28 }}
|  |  | Sootblow Optimization Safeguard Violated | [5 empty] | Min
|  |  | - | BOILER DRUM LEVEL 3<120 |  |  |  |  | Min | 1440 | 0
|  |  | - | BOILER MFT TURB TRIP(SOE)=0 |  |  |  |  | Min | 1440 | 0
|  |  | - | FURNACE PRESS #1< -10 |  |  |  |  | Min | 1440 | 0
|  |  | - | GEN ACTIVE POWER>210 |  |  |  |  | Min | 1440 | 0
|  |  | Combustion Optimization Safeguard Violated | [5 empty] | Min
|  |  | - | BOILER DRUM LEVEL 3<120 |  |  |  |  | Min | 1440 | 0
|  |  | - | BOILER MFT TURB TRIP(SOE)=0 |  |  |  |  | Min | 1440 | 0
|  |  | - | FEGT<1300 |  |  |  |  | Min | 1440 | 0
|  |  | - | FURNACE PRESS #1< -10 |  |  |  |  | Min | 1440 | 0
|  |  | - | GEN ACTIVE POWER>240 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 ID FAN FIXED BLADE POSI<97 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 ID FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 PA FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.1 PA FAN MOT CURRENT<250 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.2 ID FAN FIXED BLADE POSI<97 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.2 ID FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No.2 PA FAN MOT CURRENT<205 |  |  |  |  | Min | 1440 | 0
|  |  | - | No1 FD FAN MOT CURRENT<42 |  |  |  |  | Min | 1440 | 0
|  |  | - | No1 FD FAN MOT CURRENT>26 |  |  |  |  | Min | 1440 | 0
|  |  | - | No2 FD FAN MOT CURRENT<42 |  |  |  |  | Min | 1440 | 0
|  |  | - | No2 FD FAN MOT CURRENT>26 |  |  |  |  | Min | 1440 | 0
|  |  | - | SH.FIN.OUT HEADER L OUT GAS TEMP<800 |  |  |  |  | Min | 1440 | 0
|  |  | - | [5 empty] | Min
3 |  | Total Possible Condition Time | [6 empty] | Min | 1440.0 | 0.0
|  |  | - | Sootblow Optimization |  |  |  |  | Min | 1440.0 | 0.0
|  |  | - | Combustion Optimization |  |  |  |  | Min | 1440.0 | 0.0
4 |  | Percentage of BAT Enabled | [6 empty] | % | 92.5 | 7.5
|  |  | Percentage of Sootblow Optimization Enabled | [5 empty] | % | 92.5 | 7.5
|  |  | Percentage of Combustion Optimization Enabled | [5 empty] | % | 0.0 | 100.0
Remarks : |  |  |  | This document is generated by bot on 2022-04-15 02:02:59.
|  |  |  | Prepared By |  |  |  | Checked by |  |  |  | Witnessed / Approved by
PT . SARANA MAJU LESTARI
Name
Signature
Date